## Sheet1
line | Description | Address | type
1 | temp. hood data | 1 | 16-bit unsigned
1 | temp. hood status | 10 | 16-bit unsigned
1 | temp. chimney data | 11 | 16-bit unsigned
1 | temp. chimney status | 20 | 16-bit unsigned
1 | gas flow data | 21 | 32-bit float
1 | gas flow status | 30 | 16-bit unsigned
1 | Line Running Status | 28 | 16-bit unsigned
2 | temp. hood data | 31 | 16-bit unsigned
2 | temp. hood status | 40 | 16-bit unsigned
2 | temp. chimney data | 41 | 16-bit unsigned
2 | temp. chimney status | 50 | 16-bit unsigned
2 | gas flow data | 51 | 32-bit float
2 | gas flow status | 60 | 16-bit unsigned
2 | Line Running Status | 58 | 16-bit unsigned
3 | temp. hood data | 61 | 16-bit unsigned
3 | temp. hood status | 70 | 16-bit unsigned
3 | temp. chimney data | 71 | 16-bit unsigned
3 | temp. chimney status | 80 | 16-bit unsigned
3 | gas flow data | 81 | 32-bit float
3 | gas flow status | 90 | 16-bit unsigned
3 | Line Running Status | 88 | 16-bit unsigned
4 | temp. hood data | 91 | 16-bit unsigned
4 | temp. hood status | 100 | 16-bit unsigned
4 | temp. chimney data | 101 | 16-bit unsigned
4 | temp. chimney status | 110 | 16-bit unsigned
4 | gas flow data | 111 | 32-bit float
4 | gas flow status | 120 | 16-bit unsigned
4 | Line Running Status | 118 | 16-bit unsigned
5 | temp. hood data | 121 | 16-bit unsigned
5 | temp. hood status | 130 | 16-bit unsigned
5 | temp. chimney data | 131 | 16-bit unsigned
5 | temp. chimney status | 140 | 16-bit unsigned
5 | gas flow data | 141 | 32-bit float
5 | gas flow status | 150 | 16-bit unsigned
5 | Line Running Status | 148 | 16-bit unsigned
6 | temp. hood data | 151 | 16-bit unsigned
6 | temp. hood status | 160 | 16-bit unsigned
6 | temp. chimney data | 161 | 16-bit unsigned
6 | temp. chimney status | 170 | 16-bit unsigned
6 | gas flow data | 171 | 32-bit float
6 | gas flow status | 180 | 16-bit unsigned
6 | Line Running Status | 178 | 16-bit unsigned
Duct A | temp. data | 181 | 16-bit unsigned
Duct A | temp. status | 190 | 16-bit unsigned
Duct A | current data | 191 | 32-bit float
Duct A | current status | 200 | 16-bit unsigned
Duct A | Duct Running Status | 198 | 16-bit unsigned
Duct B | temp. data | 201 | 16-bit unsigned
Duct B | temp. status | 210 | 16-bit unsigned
Duct B | current data | 211 | 32-bit float
Duct B | current status | 220 | 16-bit unsigned
Duct B | Duct Running Status | 218 | 16-bit unsigned
Status Description : |  | 0 | Disconnected
|  | 1 | Connected
|  | 2 | Maintenance
|  | 3 | Low Limit Alarm
|  | 4 | High Limit Alarm
Line Running Description : |  | 0 | Stop
|  | 1 | Run
Duct Running Description : |  | 0 | Stop
|  | 1 | Run
|  | 2 | Alarm Blow OFF Before Timing
|  | 3 | Alarm Blow ON Over Timing

## Sheet2
Line | Description | Node Address | Line | Description | Holding Register
1 | temp. hood | 1 | 1 | temp. hood | 1
1 | temp. chimney | 11 | 1 | temp. chimney | 1
1 | gasflow | 21 | 1 | gasflow | 1
2 | temp. hood | 10 | 2 | temp. hood | 1
2 | temp. chimney | 12 | 2 | temp. chimney | 1
2 | gasflow | 22 | 2 | gasflow | 1
3 | temp. hood | 13 | 3 | temp. hood | 1
3 | temp. chimney | 23 | 3 | temp. chimney | 1
3 | gasflow | 3 | 3 | gasflow | 1
4 | temp. hood | 14 | 4 | temp. hood | 1
4 | temp. chimney | 24 | 4 | temp. chimney | 1
4 | gasflow | 4 | 4 | gasflow | 1
5 | temp. hood | 15 | 5 | temp. hood | 1
5 | temp. chimney | 25 | 5 | temp. chimney | 1
5 | gasflow | 5 | 5 | gasflow | 1
6 | temp. hood | 16 | 6 | temp. hood | 1
6 | temp. chimney | 26 | 6 | temp. chimney | 1
6 | gasflow | 6 | 6 | gasflow | 1
duct A | temp. | 17 | duct A | temp. | 1
duct A | current | 28 | duct A | current | 3000
duct B | temp. | 27 | duct B | temp. | 1
duct B | current | 29 | duct B | current | 3000

## Sheet3
Classification | Error Code | Cause | Remedy
Exception response error | 0001H | A slave station sent an unsupported function | Check the specifications of the slave station, and use appropriate functions
| 0002H | A slave station sent an unsupported device. | Check the specifications of the slave station, and specify addresses of appropriate devices
| 0003H | A slave station sent an unsupported number of devices to read or write | Check the specifications of the slave station, and then specify the number of devices to read or write
| 0004H | The slave station is in a state from which it cannot recover | If you cannot recover the slave unit by restarting its power, contact the manufacturer of the slave unit.
Parameter error | 0101H | • A value outside of the range 1 to 247 was specified for the slave station number. • Broadcast station number 0 was specified when a device was read | Check the value of the specified slave station number (CM5001, CM6001, or CM7001).
| 0102H | An unsupported function code was specified. | Check the value of the specified function code (CM5002, CM6002, or CM7002).
| 0103H | [Read coil or read input] A value outside of the range 1 to 2000 was specified for the number of devices to read. [Read holding register or read input register] A value outside of the range 1 to 125 was specified for the number of devices to read. [Write continuous coils] A value outside of the range 1 to 1968 was specified for the number of devices to write. [Write continuous holding registers] A value outside of the range 1 to 123 was specified for the number of devices to write. | Check the specified number of devices.
Illegal reception error | 0201H | • A different command request was received on the communication line. • The response from a slave station to the previous command that was sent is slow, and the response from a different slave station to a command that was subsequently sent has been received | • A different command request was received on the communication line. • The response from a slave station to the previous command that was sent is slow, and the response from a different slave station to a command that was subsequently sent has been received
Communication error | 0301H | The data of the received command is not correct. The command may have been influenced by an external force such as noise. | Send the previous command again. If this error occurs frequently, check the communication environment, and implement counter-measures against external forces such as noise
0302H
Timeout error | 0401H | The command sent from the master station has not reached the slave station or the slave station is in a state in which it cannot recognize the command | • Check the communication line wiring. • Check whether the slave station settings, such as the communication speed and parity, are the same as those on the master station. • Check the number of the slave station.

## Sheet4
PLC | 192.168.0.10 |  |  | to | d200
HMI | 192.168.0.11
PLC OMRON | 192.168.0.20 | from | d2000